CH-C-0100-0201                     * CH-C-0100-0201 is a Hall-Effect current transducer.

Current Transducer                              * It can be used for the detection of DC, AC, pulse.

| Electrical data |
| --- |
| IPN | Primary nominal r.m.s current |  |  |  | 100 | A |
| IP | Primary current, measuring range |  |  |  | 0…( 150 | A |
| ISN | Secondary nominal r.m.s current |  |  |  | 50 | mA |
| KN | Conversion ratio |  |  | 1:2000 |  |
| VC | Supply voltage (( 5%) |  |  |  | ( 12…( 15 | V |
| IC | Idle Current consumption |  |  |  | 15 (@( 15) | mA |
| Vd | AC isolation test, 50 Hz, 1min |  | 3 | kV |
| RM | Measuring resistance @ | TA = 100(C |  |  |
|  |  |  | RM min |  | RM max |  |
|  | with ( 12V | @(100Amax | 0 |  | 126 | ( |
|  |  | @(150 Amax | 0 |  | 52 | ( |
|  | with ( 15 V | @(100 Amax | 0 | 182 | ( |
|  |  | @(150Amax | 0 | 90 | ( |

| Accuracy – Dynamic performance data |
| --- |
| X | Accuracy @ IPN , TA = 25(C | @ ( 15V (( 5%) | ( 0.40 | % |
| (L | Linearity |  | < 0.15 | % |
| IO | Offset current @ IP = 0, TA = 25(C @(100 Amax 0 0 | ( 0.20 |  | mA |
| IOM | Residual current @ IP = 0, after an overload of 3 ( IPN 0 | ( 0.30 | mA |
| IOT | Thermal drift of IO @(100 Amax | (-10℃…+100℃) | ( 0.40 |  | mA |
| tr | Response time @ 90% of IPN |  |  |  | <3 | (s |
| di/dt | di/dt accurately followed |  | >100 | A/(s |
| f | Frequency bandwidth (-1 dB) |  | DC…100 | kHz |

| General data |
| --- |
| TA | Ambient operating temperature |  | -10..+100 | (C |
| m | Mass |  | 25 | g |

Remarks

- IS is positive when IP flows in the direction of the arrow.

- Temperature of the primary conductor should not exceed 100 (C.

# Text boxes

IPN = 100 A

Applications

- AC variable speed drives and servo motor drives

- Static converters for DC motor drives

- Battery supplied applications

- Uninterruptible Power Supplies(UPS)

- Switched Mode Power Supplies (SMPS)

- Power supplies for welding applications.

Features

- Closed loop (compensated) current transducer using the Hall-Effect

Advantages

- Excellent accuracy

- Very good linearity

- Low temperature drift

Special features

- Printed circuit board mounting.

* * * * * * * * * * * * * * * * * *

### SECONDARY TERMINALS

TERMINAL +：SUPPLY VOLTAGE +12…15V

TERMINAL M：MEASURE

TERMINAL -：SUPPLY VOLTAGE  -12…15V